## Coil
Conductor pack width | m | 0.123
Conductor pack height | m | 0.176
Fraction of area to conductors |  | 0.63476
Fraction of area to structure |  | 0.36524
Jacket thickness | m | 0.002
Insulation thickness | m | 0.0025
#Turns |  | 6
Base peak current | Amp-turn | 90000
Form factor (rms/peak) |  | 1
Base total current | Amp-turn rms | 90000
Jacket OD | m | 0.054
Jacket OD | in | 2.126
Jacket ID | m | 0.05
Jacket ID | in | 1.9685
Jacket area | m2 | 0.00032673
Conductor OD | m | 0.045
Conductor OD | in | 1.7717
Conductor ID | m | 0.03
Conductor ID | in | 1.1811
Fraction ID/OD |  | 0.66667 |  | Jacket OD | mm | 54
Fraction ID/OD allowable |  | 0.66667 |  | Jacket thickness | mm | 2
Conductor area | m2 | 0.00088357 |  | Insulation thickness | mm | 2.5
Cooling hole area | m2 | 0.00070686 |  | Conductor OD | mm | 45
Conductor length per turn | m | 10.8851 |  | Conductor ID | mm | 30
Conductor length per turn | ft | 35.7121 |  | Conductor length per turn | m | 10.8851
Feeder length per pole | m | 20 |  | Feeder length per pole | m | 20
Feeder length per pole | ft | 65.6168 |  | #Sub-circuits |  | 1
#Sub-circuits |  | 1 |  | #Turns per sub-circuit |  | 6
#Turns per sub-circuit |  | 6 |  | Total conductor length per sub-circuit | m | 105.3104
Total conductor length per sub-circuit | m | 105.3104 |  | Total conductor length per sub-circuit | ft | 345.5065
Total conductor length per sub-circuit | ft | 345.5065 |  | #Sub-circuits in series hydraulically |  | 1
#Sub-circuits in series hydraulically |  | 1 |  | #Sub-circuits in parallel hydraulically |  | 1
#Sub-circuits in parallel hydraulically |  | 1 |  | #Sub-circuits in series electrically |  | 1
#Sub-circuits in series electrically |  | 1 |  | #Sub-circuits in parallel electrically |  | 1
#Sub-circuits in parallel electrically |  | 1 |  | Base total current | Amp-turn rms | 90000
#Turns effective |  | 6 |  | #Turns effective |  | 6
Base current | Amp rms | 15000 |  | Per unit current | p.u. | 1
Per unit current | p.u. | 1 |  | Current per turn effective | Amp rms | 15000
Current per turn effective | Amp rms | 15000 |  | Current per sub-circuit | Amp rms | 15000
Current per sub-circuit | Amp rms | 15000 |  | Net series/parallel circuit resistance at 20C | mOhm | 2.0549
Flow velocity | feet/sec | 22.1408 |  | Flow velocity | m/s | 6.7485
Flow velocity | m/s | 6.7485 |  | Water Inlet Temperature | deg C | 100
Allowable flow velocity | m/s | 8 |  | delta_T | deg C | 40
Flow per sub-circuit | m3/s | 0.0047703 |  | Net series/parallel circuit resistance at average resistivity | mOhm | 2.8974
Flow per sub-circuit | GPM | 75.618 |  | Total ohmic dissipation | kW | 651.9178
Mass flow per sub-circuit | kg/s | 4.304 |  | Volumetric nuclear heating rate | watt/cc | 0.5
Water Inlet Temperature | deg C | 100 |  | Total metallic area | m2 | 0.015168
Allowable Water Outlet Temperature | deg C | 140 |  | Total metallic volume | m3 | 0.16511
Water Average Temperature | deg C | 120 |  | Total nuclear heating | kW | 82.5548
cs0 |  | 4229.2 |  | Total heat load | Watt | 734.4726
cs1 |  | -3.857 |  | Heat load per hydraulic circuit | Watt | 734.4726
cs2 |  | 0.06786 |  | delta_T | deg C | 40
cs3 |  | -0.0003745 |  | Maximum temperature | deg C | 140
cs4 |  | 8.1906e-07 |  | delta_T/sec (LOCW) | degC/sec | 2.183
Specific Heat | J/kg-C | 4266.2483 |  | Hydraulic path delta_P | MPA | 0.86493
cv0 |  | 0.0017887 |  | Boiling Pressure at Outlet Temp | MPA | 0.35894
cv1 |  | -5.1271e-05 |  | Return pressure | MPA | 0.71788
cv2 |  | 7.9112e-07 |  | Inlet pressure | MPA | 1.6862
cv3 |  | -6.752e-09
cv4 |  | 3.1597e-11
cv5 |  | -7.5437e-14
cv6 |  | 7.1718e-17
Water Dynamic Viscosity | kG/m-s | 0.00024986
cd0 |  | 1005.4
cd1 |  | -0.539
cd2 |  | -0.0026713
Water Density | kg/m3 | 902.2533
Water Kinematic Viscosity | m2/s | 2.7692e-07
Water Reynold's Number |  | 731088.8983
Water Friction Factor |  | 0.01082
Hydraulic path delta_P | PA | 864930.8802
Hydraulic path delta_P | psi | 125.4476
Plumbing Water Pressure Drop | psi | 15
Total Pressure Drop | psi | 140.4476
A1 |  | 8.0713
B1 |  | 1730.63
C1 |  | 233.426
A2 |  | 8.1402
B2 |  | 1810.94
C2 |  | 244.485
A |  | 8.1402
B |  | 1810.94
C |  | 244.485
Boiling Pressure at Outlet Temp | psi | 52.0601
Boiling Pressure at Outlet Temp | PA | 358941.9984
Return pressure multiple of boiling |  | 2
Return pressure | psi | 104.1203
Return pressure | PA | 717883.9968
Inlet pressure | psi | 244.5679 | http://ddbonline.ddbst.de/AntoineCalculation/AntoineCalculationCGI.exe?component=Water
Inlet pressure | PA | 1686236.2363
Allowable inlet pressure | psi | 1000
Water thermal resistance | Watt/deg C | 18361.8222
100% IACS Resistivity at 20C | ohm-m | 1.7241e-08
%IACS |  | 100%
Resistivity at 20C | ohm-m | 1.7241e-08
Net series/parallel circuit resistance at 20C | ohm | 0.0020549
Temp Coefficient of Resistivity | per deg C | 0.0041
Average Resisitivity | ohm-m | 2.431e-08
Net series/parallel circuit resistance at average resistivity | ohm | 0.0028974
Total ohmic dissipation | Watt | 651917.7735
Volumetric nuclear heating rate | watt/cc | 0.5
Conductor metallic area per turn | m2 | 0.0012103
Structure metallic area | m2 | 0.0079067
Total metallic area | m2 | 0.015168
Total metallic volume | m3 | 0.16511
Total nuclear heating | Watt | 82554.8405
Total heat load | Watt | 734472.614
Heat load per hydraulic circuit | Watt | 734472.614
delta_T | deg C | 40
Allowable delta_T | deg C | 40
Maximum temperature | deg C | 140
Cu temp coefficient of specific heat | per deg C | 0.105
Cu 20C specific heat | J/kg-degC | 393.5
Cu specific heat at avg temp | J/kg-degC | 404
Cu density | kg/m3 | 8950
Cu heat capacity | J/degC | 336447.9969
delta_T/sec (LOCW) | degC/sec | 2.183

## Bus_Bar
Conductor width | m | 0.05 | Conductor width | m | 0.05
Conductor height | m | 0.1 | Conductor height | m | 0.1
Aspect ratio |  | 2 | Cooling hole diameter | m | 0.0175
Cooling hole diameter | m | 0.0175 | Max length of single conductor section | m | 5.8689
Cooling hole diameter | in | 0.68898 | Current | Amp rms | 15000
Conductor area | m2 | 0.0047595 | Avg conductor length per pole | m | 30.3333
#Conductor in parallel electrically and hydraulically per pole |  | 2 | #Conductor in parallel electrically and hydraulically per pole |  | 2
#Poles in series hydraulically |  | 2 | Resistance per pole at 20C | mOhm | 0.054941
Total length per pole pair | m | 657 | Flow velocity | m/s | 2.7801
Number of pole pairs |  | 27 | Flow per conductor | m3/s | 0.00066869
Shaft to chimney allowance | m | 6 | Mass flow per conductor | kg/s | 0.66082
Avg conductor length per pole | m | 30.3333 | #Poles in series hydraulically |  | 2
fraction cooling hole dia / min(width, height) |  | 0.35 | Hydraulic path delta_P | MPA | 0.24741
Fraction allowable |  | 0.375 | Return pressure | MPA | 0.02461
Current | Amp rms | 15000 | Inlet pressure | MPA | 0.37544
Flow velocity | feet/sec | 9.121 | Water Inlet Temperature | deg C | 45
Flow velocity | m/s | 2.7801 | Water delta_T | deg C | 5
Allowable flow velocity | m/s | 4 | Resistance per pole at average temperature | mOhm | 0.061135
Cooling hole area | m2 | 0.00024053 | Ohmic dissipation per pole | kW | 13.7554
Flow per conductor | m3/s | 0.00066869 | Ohmic dissipation per unit length | kW/m | 0.45348
Flow per conductor | GPM | 10.6001 | Total # bus bar poles |  | 2
Mass flow per conductor | kg/s | 0.66082 | Total ohmic dissipation, fraction of total coil + bus bar |  | 0.040491
Water Inlet Temperature | deg C | 45 | Total flow | m3/s | 0.0026748
Allowable Water Outlet Temperature | deg C | 50 | Total mass flow | kg/s | 2.6433
Water Average Temperature | deg C | 47.5 | Total bus bar resistance at 20C | ohm | 0.00010988
cs0 |  | 4229.2 | Total bus bar resistance at average temperature | ohm | 0.00012227
cs1 |  | -3.857 | Total coil resistance at 20C | ohm | 0.0020549
cs2 |  | 0.06786 | Total coil resistance at average temperature | ohm | 0.0028974
cs3 |  | -0.0003745 | Total circuit resistance at 20C | ohm | 0.0021648
cs4 |  | 8.1906e-07 | Total circuit resistance at average temperature | ohm | 0.0030197
Specific Heat | J/kg-C | 4163.1353
cv0 |  | 0.0017887
cv1 |  | -5.1271e-05
cv2 |  | 7.9112e-07
cv3 |  | -6.752e-09
cv4 |  | 3.1597e-11
cv5 |  | -7.5437e-14
cv6 |  | 7.1718e-17
Water Dynamic Viscosity | kG/m-s | 0.0005581
cd0 |  | 998.0853
cd1 |  | -0.061254
cd2 |  | -0.0030762
Water Density | kg/m3 | 988.2351
Water Kinematic Viscosity | m2/s | 5.6475e-07
Water Reynold's Number |  | 86147.5351
Water Friction Factor |  | 0.018468
Hydraulic path delta_P | PA | 247413.9334
Hydraulic path delta_P | psi | 35.8844
Plumbing Water Pressure Drop | psi | 15
Total Pressure Drop | psi | 50.8844
A1 |  | 8.0713
B1 |  | 1730.63
C1 |  | 233.426
A2 |  | 8.1402
B2 |  | 1810.94
C2 |  | 244.485
A |  | 8.0713
B |  | 1730.63
C |  | 233.426
Boiling Pressure at Outlet Temp | psi | 1.7847
Boiling Pressure at Outlet Temp | PA | 12304.8452
Return pressure multiple of boiling |  | 2
Return pressure | psi | 3.5693
Return pressure | PA | 24609.6904
Inlet pressure | psi | 54.4537
Inlet pressure | PA | 375444.983
Allowable inlet pressure | psi | 100
Allowable inlet pressure | PA | 689475.728
Water thermal resistance per pole | Watt/deg C | 5502.1817
100% IACS Resistivity at 20C | ohm-m | 1.7241e-08
%IACS |  | 100%
Resistivity at 20C | ohm-m | 1.7241e-08
Resistance per pole at 20C | ohm | 5.4941e-05
Temp Coefficient of Resistivity | per deg C | 0.0041
Average Resisitivity | ohm-m | 1.9185e-08
Resistance per pole at average temperature | ohm | 6.1135e-05
Ohmic dissipation per pole | Watt | 13755.4232
Ohmic dissipation per unit length | kW/m | 0.45348
#Coils in circuit |  | 1
# Interleaves per coil |  | 1
Total # bus bar poles |  | 2
Total ohmic dissipation, fraction of total coil + bus bar |  | 0.040491
Water delta_T | deg C | 5
Allowable delta_T | deg C | 5
Cu temp coefficient of specific heat | per deg C | 0.105
Cu 20C specific heat | J/kg-degC | 393.5
Cu specific heat at avg temp | J/kg-degC | 396.3875
Cu density | kg/m3 | 8950
Cu heat capacity | J/degC | 512179.1354
delta_T/sec (LOCW) | degC/sec | 0.026857
Total flow | m3/s | 0.0026748
Total mass flow | kg/s | 2.6433
Total bus bar resistance at 20C | ohm | 0.00010988
Total bus bar resistance at average temperature | ohm | 0.00012227
Max billet | kg | 250
Max length of single conductor section | m | 5.8689

## Coil_Dims
Coils |  | Upper | Equatorial | Lower
Conductor pack height | m | 0.176 | 0.176 | 0.176
r1 | m | 7.8065 | 8.7257 | 8.3156
z1 | m | 3.441 | 1.8279 | -1.5852
r2 | m | 8.3441 | 8.7669 | 7.8476
z2 | m | 2.6727 | -0.59195 | -2.4362
dtheta | degrees | 28.5 | 20 | 30
Upper toroidal length | m | 3.8393 | 3.0151 | 4.308
Lower toroidal length | m | 4.1067 | 3.0295 | 4.0629
Average toroidal length | m | 3.973 | 3.0223 | 4.1854
Poloidal length | m | 0.93766 | 2.4202 | 0.97122
Length per turn | m | 9.8214 | 10.8851 | 10.3133

## Inductances
Coil
Average toroidal length | m | 3.973 | 3.0223 | 4.1854
Poloidal length | m | 0.93766 | 2.4202 | 0.97122
Conductor pack width | m | 0.123 | 0.123 | 0.123
Conductor pack height | m | 0.176 | 0.176 | 0.176
Effective radius | m | 0.046834 | 0.046834 | 0.046834
One-turn inductance | henry | 5.8653e-06 | 7.6783e-06 | 6.2394e-06 | Grover, p. 60
#Turns |  | 6 | 6 | 6
Multi-turn inductance | henry | 0.00021115 | 0.00027642 | 0.00022462
Grover ex. 22
| 15 | 6 | 6 | 6
a | 10 | 397.3033 | 302.231 | 418.5447
a1 | 5 | 93.7658 | 242.0221 | 97.1219
b | 3 | 17.6 | 17.6 | 17.6
g | 11.1803 | 408.2181 | 387.1928 | 429.6654
| 30 | 609.6025 | 1196.944 | 665.1796
| 0.57567 | 0.35761 | 0.12862 | 0.34997
| 0.19257 | 0.052599 | 0.09654 | 0.050657
| 0.69781 | 5.4839 | 7.1455 | 5.7412
| 0.70111 | 2.632 | 6.2656 | 2.7278
| -1.203 | -5.729 | -7.1976 | -5.9795
| -0.80202 | -2.6397 | -6.296 | -2.735
| 0.60706 | 0.19069 | 0.092991 | 0.18408
| -1.3762 | -17.2437 | -7.4916 | -18.432
| 0.06 | 0.0027716 | 0.0014116 | 0.0025401
| 0.95123 | 15.8948 | 3.5558 | 17.0352
| 0.045352 | 0.19819 | 1.8207 | 0.20265
| 0.30282 | 1.1407 | 2.1056 | 1.1846
| 2.257e-05 | 0.00020773 | 0.00027232 | 0.00022093 | Grover, p. 70
Bus Bar
Distance between conductors | m | 0.005
Effective current center spacing | m | 0.055
Effective conductor radius | m | 0.022508
Length per pole | m | 30.3333
Inductance per conductor pair | henry | 1.2014e-05 | Grover, p. 39
#Conductor in parallel electrically |  | 2
Inductance per pole pair | henry | 6.0072e-06

## Circuit
Coil resistance | ohm | 0.0028974
Coil inductance | henry | 0.00027642
Bus bar resistance | ohm | 0.00012227
Bus bar inductance | henry | 6.0072e-06
Total circuit resistance | ohm | 0.0030197
Total circuit inductance | henry | 0.00028242
Current per turn | amp | 15000
AC Mode
Frequency | Hz | 5
Inductive reactance | ohm | 0.0088726
Complex impedance | ohm | 0.0093724
Load power factor |  | 0.32219
Phase angle |  | 71.2047
Voltage drop | volt | 140.5861
Current at peak voltage | amp | 4832.8294
Power supply regulation at full load |  | 0.2
Power supply regulation at current at peak voltage |  | 0.064438
Min power supply no-load voltage |  | 150.2691
Selected PS voltage |  | 180
Active power | watt | 339714.3099
Apparent power | volt-amp | 2700000
Reactive power | volt-amp-reactive | 2678543.2958
Net power factor |  | 0.12582
DC Mode
Voltage drop | volt | 45.2952
Active power | watt | 679428.6198
Apparent power | volt-amp | 2700000
Reactive power | volt-amp-reactive | 2613116.2911
Net power factor |  | 0.25164

## ELM_Design_Point
ELM COIL
Conductor pack width | m | 0.123
Conductor pack height | m | 0.176
Jacket OD | mm | 54
Jacket thickness | mm | 2
Insulation thickness | mm | 2.5
Conductor OD | mm | 45
Conductor ID | mm | 30
Conductor length per turn | m | 10.8851
Feeder length per pole | m | 20
#Sub-circuits |  | 1
#Turns per sub-circuit |  | 6
Total conductor length per sub-circuit | m | 105.3104
#Sub-circuits in series hydraulically |  | 1
#Sub-circuits in parallel hydraulically |  | 1
#Sub-circuits in series electrically |  | 1
#Sub-circuits in parallel electrically |  | 1
Base total current | Amp-turn rms | 90000
#Turns effective |  | 6
Per unit current | p.u. | 1
Current per turn effective | Amp rms | 15000
Current per sub-circuit | Amp rms | 15000
Net series/parallel circuit resistance at 20C | mOhm | 2.0549
Flow velocity | m/s | 6.7485
Water Inlet Temperature | deg C | 100
delta_T | deg C | 40
Net series/parallel circuit resistance at average resistivity | mOhm | 2.8974
Total ohmic dissipation | kW | 651.9178
Volumetric nuclear heating rate | watt/cc | 0.5
Total metallic area | m2 | 0.015168
Total metallic volume | m3 | 0.16511
Total nuclear heating | kW | 82.5548
Total heat load | Watt | 734.4726
Heat load per hydraulic circuit | Watt | 734.4726
delta_T | deg C | 40
Maximum temperature | deg C | 140
delta_T/sec (LOCW) | degC/sec | 2.183
Hydraulic path delta_P | MPA | 0.86493
Return pressure | MPA | 0.71788
Inlet pressure | MPA | 1.6862
ELM BUS BAR
Conductor width | m | 0.05
Conductor height | m | 0.1
Cooling hole diameter | m | 0.0175
Current | Amp rms | 15000
Avg conductor length per pole | m | 30.3333
#Conductor in parallel electrically and hydraulically per pole |  | 2
Resistance per pole at 20C | mOhm | 0.054941
Flow velocity | m/s | 2.7801
Flow per conductor | m3/s | 0.00066869
Mass flow per conductor | kg/s | 0.66082
#Poles in series hydraulically |  | 2
Hydraulic path delta_P | MPA | 0.24741
Return pressure | MPA | 0.02461
Inlet pressure | MPA | 0.37544
Water Inlet Temperature | deg C | 45
Water delta_T | deg C | 5
Resistance per pole at average temperature | mOhm | 0.061135
Ohmic dissipation per pole | kW | 13.7554
Ohmic dissipation per unit length | kW/m | 0.45348
Total # bus bar poles |  | 2
Total ohmic dissipation, fraction of total coil + bus bar |  | 0.040491
Total flow | m3/s | 0.0026748
Total mass flow | kg/s | 2.6433
Total bus bar resistance at 20C | ohm | 0.00010988
Total bus bar resistance at average temperature | ohm | 0.00012227
Total bus bar inductance | henry | 0.0020549
TOTAL ELM CIRCUIT
Coil resistance | ohm | 0.0028974
Coil inductance | henry | 0.00027642
Bus bar resistance | ohm | 0.00012227
Bus bar inductance | henry | 6.0072e-06
Total circuit resistance | ohm | 0.0030197
Total circuit inductance | henry | 0.00028242
Current per turn | amp | 15000
AC Mode
Frequency | Hz | 5
Inductive reactance | ohm | 0.0088726
Complex impedance | ohm | 0.0093724
Load power factor |  | 0.32219
Phase angle |  | 71.2047
Voltage drop | volt | 140.5861
Current at peak voltage | amp | 4832.8294
Power supply regulation at full load |  | 0.2
Power supply regulation at current at peak voltage |  | 0.064438
Min power supply no-load voltage |  | 150.2691
Selected PS voltage |  | 180
Active power | watt | 339714.3099
Apparent power | volt-amp | 2700000
Reactive power | volt-amp-reactive | 2678543.2958
Net power factor |  | 0.12582
DC Mode
Voltage drop | volt | 45.2952
Active power | watt | 679428.6198
Apparent power | volt-amp | 2700000
Reactive power | volt-amp-reactive | 2613116.2911
Net power factor |  | 0.25164
TOTAL ELM SYSTEM
# coils |  | 27
Simultaneity factor |  | 0.5
Total input active power | watt | 9172286.3676
Total input reactive power | volt-amp-reactive | 72320668.9874
Total input apparent power | volt-amp | 72900000
Total ohmic + nuclear heat load from coils to TCWS | watt | 11029870.6362
Total mass flow to coils from TCWS | kg/s | 116.2073
Total heat load from bus bar to CCWS | watt | 371396.4258
Total mass flow to bus bar from CCWS | kg/s | 71.3688