## Slide 1: ITER In-Vessel Coils (IVC) Interim Design Review Integration with Interfacing Systems
C Neumeyer
July 28, 2010

## Slide 2: Outline
Interfacing Systems and Open Issues
Issues and Resolution Plan Summary

## Slide 3
Tokamak
CWS
Component
CWS
Plasma Control
Local
Control
CODAC
Central
Interlock
SSEN
PPEN
UPS
Local
Interlock
400kV
Grid
Cryostat
VV
Plasma
Coil Jacket
Coil
Jacketed Feeder typ.
Flow
& Temp
Typ.
DCCT typ.
AC/DC
Conv
DC Bus
Port Bulkhead/Vacuum feed-thrus
Coil-feeder
Jumpers typ.

## Slide 4: Primary Interfaces
Coil Power Supply & Distribution System (CPSDS) PBS 41
  Current flow through DC bus bar input/output
  Measurement of voltage and current
  Grounding and ground fault detection
  Switches and links for isolation and grounding
Tokamak Cooling Water System (TCWS) PBS 26
  Water flow through insulating supply/return lines
  Measurement of pressure, flow, temperature, chemistry and conductivity
  Valves for isolation and draining
  Draining and drying
Vacuum vessel (VV) PBS 31
  Structural support
  Vacuum feed-thru’s for feeders at port penetrations
CODAC PBS 45
  Pressure, flow, temperature, voltage, current, input power, cooling power, ground current, etc.
Central Interlock System (CIS) PBS 46
  Fault status (multi-level)

## Slide 5: Integration with CPSDS
Voltage, current, power described by design point spreadsheets
VS power supply implementation previously studied and presented at CDR
              Extension of VS chopper concept to two interleaves now being studied
ELM power supply is standard thyristor rectifier
Grounding and ground fault detection is new issue now being addressed

## Slide 6: Grounding and Ground Fault Detection
Typical method relies on high resistance grounding from each terminal to ground
E
V-gnd
x
E/2
-E/2
V-gnd
x
E
0
a
b
a
b
normal
fault
a
b
b
a
E
I=0
I≠0
RG1
RG2
RG1
RG1
RG2
RG1
Ground fault detection by measuring ground current
Sensitivity set by selection of grounding resistors RG

## Slide 7: Grounding and Ground Fault Detection
Resistance of
  Relatively low and highly variable resistance to ground
    MIC insulation resistivity varies substantially with both radiation (RIC) and temperature
    Cooling water has relatively low conductivity at high temperatures and strong temperature dependence
  All turns directly face ground since MIC is jacketed
    Stray capacitance to ground is relatively high
  Chopper power supply (VS)
RG1
RG2
E
I
Cstray
Rstray
Rwater_return
Cstray
Rstray
Rwater_supply
RG1
Rwater will vary with T
Rstray will vary with radiation
Asymmetry in Rwater and Rstray will appear as ground fault
RG will determine selectivity between asymmetry effects and true ground fault

## Slide 8: Grounding and Ground Fault Detection
Water initially at 5MΩ-cm at RT will decrease by factor of 8.7 at 100oC
Water initially at 5MΩ-cm at RT will decrease by factor of 20 at 150oC
With 100oC supply and 150oC return the resistivity ratio will be 2.3
Will result in asymmetry in stray insulation resistance to ground
Courtesy of
Andre Petrov
ORNL

## Slide 9: Grounding and Ground Fault Detection
Ratio of un-irradiated mineral insulation resistivity at 150oC
vs. 100oC ~ 25
Will result in asymmetry in stray resistance to ground
From Tyco Pyrotenax
Engineering Guide, p. 12

## Slide 10: Grounding and Ground Fault Detection
Ratio of un-irradiated mineral insulation resistivity to radiated at 100 Gy/s is approximately 10,000
Asymmetry effect in stray insulation resistance to ground will depend on distribution of flux along winding
L. Snead et al, ORNL, CRADA Report 94-0301,
“Improved Mineral Insulated Cables for High Radiation Environment”, Fig. 2

## Slide 11: Grounding and Ground Fault Detection
Radiation flux varies along turns of winding by ~ factor of 2
Advantageous to place turns with maximum exposure toward voltage null and to distribute with symmetry about null
Voltage null
Nuclear heating in VS bundle

## Slide 12: Grounding and Ground Fault Detection
Choice of grounding resistance, water supply/return resistance, and ground fault detection scheme has to consider
  Resistance variation with temperature and radiation, both symmetric and asymmetric components
  Stray capacitance effects
Available data suggests that stray insulation resistance of SSMIC may decrease
to several 10’s of kilohms under high temperature irradiated conditions

## Slide 13: Grounding and Ground Fault Detection
Work now underway to evaluate VS grounding and ground fault detection using PSCAD simulation tool, including chopper power supply model
For hipot testing, four conditions should be considered
  Un-irradiated, bakeout (~ 200oC)
  Un-irradiated, ready for operations (100oC)
  Un-irradiated, room temperature (25oC)
  Un-irradiated, drained and dry (25oC)

## Slide 14: Integration with TCWS
Flow, pressure, temperature, wetted Cu area, etc., described by design point spreadsheets
Cooling water resistivity should be ~ 5MΩ-cm at 25oC
Supply/return insulating break geometry and implementation remains an open issue
Diameter could be reduced, e.g. to 20mm, to increase R by (30/20)^2=2.25 but the flow velocity would increase by the same factor

## Slide 15: Integration with TCWS
Water supply/return design remains an open issue
  Ceramic-based design favored for radiation and chemical resistance
    Would require feature to allow for thermal expansion
    Would require containment in case of cracking
      TCWS can be contaminated with T
Water line configuration
Used at LAMPF
Commercial product from Ceramaseal

## Slide 16: Integration with TCWS
Water supply/return design remains an open issue
  Custom design based on IVC requirement is needed
  Large ceramic tubes are available
http://www.sentrotech.com/

## Slide 17: Interface with VV Ports and DC Bus and TCWS
Bolted Connection at ELM/VS Pole
  Provides clamping force for electrical connection
Flexible Length
  Minimize length
  Allow compliance
Rigid Bus Bar
  + pole has cooling water supply
  - pole has cooling water return
  Water “jumper” needs electrical isolation between supply/return
Flexible Bus Bar
End of Bus Bar (green)
Bolted Connection to ELM/VS Pole
Water Jumper (red)
Cartoon-level design needs further development

## Slide 18: Issues and Resolution Plan
Issue | Resolution | Pre/Post October
Determine optimum resistance values for grounding resistors and water supply/return lines for ELM and VS | Perform studies to investigate effect of resistance on ground current in normal and ground fault modes for ELM and VS | Pre
Develop agreement on scope boundary for interfaces (e.g. supply/return lines, electrical and hydraulic measurements, local I&C | Discuss with interfacing PBS RO’s and reflect in SRD/ICDs | Pre
Develop design for water supply/return lines for ELM and VS | Develop designs and perform R&D to fabricate prototype | Post (out of scope of present task, but required for FDR)
Develop design for feed-through of feeders through port covers | Perform detailed design activity | Post (out of scope of present task, but required for FDR)
Develop design for electrical connection to DC bus bar | Perform detailed design activity | Post (out of scope of present task, but required for FDR
Develop local interlock and I&C plan for IVC | Determine appropriate measurements, identify instruments, develop interlock logic, determine CODAC interface | Post (out of scope of present task, but required for FDR)

## Slide 19: Summary
ICD development underway
Some technical issues remain unresolved
  Grounding and ground fault detection
Some design details remain incomplete
  Design concept for water supply/return lines with insulating breaks
  Port vacuum feed-thru’s
  DC bus bar connections