Procedure Title: ECS HCS INPUT/OUTPUT CHECKOUT

| Number: OP-PC-44 | Revision: 3 | Effective Date: 11/12/98 (Ref. OP-AD-97 Expiration Date: (2 yrs. unless otherwise stipulated) |
| --- | --- | --- |

Procedure Approvals

| Author C Neumeyer | Date |
| --- | --- |

| ATI S Ramakrishnan | Date |
| --- | --- |

| RLM C Neumeyer | Date |
| --- | --- |

Responsible Division: NSTX WBS-5

Procedure Requirements designated by RLM

|  | NSTX Work Permit (TBD) | x | Lockout/Tagout (OP-AD-61) |
| --- | --- | --- | --- |

|  | TFTR Work Permit (OP-AD-09) |  | Door Permit (OP-G-93) |
| --- | --- | --- | --- |

|  | Tritium Work Permit (OP-AD-49) | x | T-Mod (OP-AD-03) |
| --- | --- | --- | --- |

|  | RWP (HP-OP-20) |  | Lift Procedure (ENG-021) |
| --- | --- | --- | --- |

|  | Confined Space Permit |  | DCA/DCN (OP-AD-104) |
| --- | --- | --- | --- |

|  | Pre-Job Brief (OP-AD-79) |  | ATI Walkdown |
| --- | --- | --- | --- |

|  | USQD (OP-AD-63) |  | Independant Review |
| --- | --- | --- | --- |

|  | Master Equip. List Mod (OP-AD-112) |  | ES&H Review (NEPA, IH, etc.) |
| --- | --- | --- | --- |

Engineering In Charge (EIC): ______________________ Date: ______/_______/_______ Special Instructions:

REVIEWERS (designated by RLM)

ATI - S Ramakrishnan

Test Director –

Independent Reviewer

D-Site Shift Supervisor

NSTX –

TFTR Caretaking

Vacuum

Computer

Tritium

QA/QC

AC Power –

FED

ECS/MG – J Corl

ERWM

Water

NB

RF

Diagnostics

TRAINING (designated by RLM)

| No training required ______________ | Instructor _____________________________ |
| --- | --- |

| Personnel (group, job title or individual name) | Read Only | Instruction | Hands On |
| --- | --- | --- | --- |

| FCPC Technicians and Engineers | x |  |  |
| --- | --- | --- | --- |

Training Rep. ____________________________________

RLM___________________________________

1.0 	PURPOSE

To confirm integrity of interfaces between the Hardwire Control Systems (HCS) and the ECS thyristor rectifiers.

2.0 	SCOPE

This procedure covers all ECS subsystems.

3.0 	REFERENCE STANDARDS

3.1	None.

4.0	 PREREQUISITES

4.2 	HCS, Thyristor Rectifier, Halmar, RIS/ACP control power ON.

5.0 	SAFETY PRECAUTIONS

5.1	 System shall be in a safe state per AP-ECS-01

6.0 	PROCEDURE

Note : Perform on one subsystem at a time and record on list.

6.1	Inspect HCS control boards. Check for any jumpers. If jumpers exist determine need and repair if possible. Otherwise if jumper is to remain confirm presence of T-mod.

6.2 	Place all subsystem Rectifier HCS Defeaters in the "TEST" (isolated) position.

6.3	Clear all Level 3 faults on power supplies, clear all Level 1 faults on equipment other than power supplies (ie RIS, ACP, EFDS, Halmar imbalance, Halmar control power).

6.4 	Defeat HCS K4 relay so as to generate enable signal.

6.5 	Reset HCS Level 1 and Level 3 using K6 relay on HCS board. Check lamps,

replace if necessary.

6.6	On Rectifier HCS Defeater panels, confirm illumination of green LED's on L1 and L3 lines.

6.7 	On Rectifier HCS Defeater panels, turn control power OFF on one unit at  a time and confirm that no HCS faults are generated.

6.8 	Place Rectifier HCS Defeater panels the in "NORMAL" position; reset fault detectors (L1 fault, L3 clear).

6.9 	One unit at a time, turn OFF control power and confirm drop out of F3S, F3P, and F3 on HCS. On Rectifier HCS Defeater panels, confirm L3 red LED illuminated. Reset fault detectors (L1 fault, L3 clear).

6.10	On Rectifier HCS Defeater panels, momentarily switch bat handle to NORMAL and  confirm L1 red LED illuminated. Reset fault detectors (L1 fault, L3 clear).

6.11 	Confirm "permissive" LED not illuminated on all fault detectors.

6.12 	Reset all rectifiers (clear rectifier L3 faults), clear HCS L1 and L3 faults. Insert "red key" in 69TPS relay to simulate permissive signal. Confirm "permissive" LED illuminated on fault detectors. Confirm HCS control panel lamp. Confirm "FD Ready Glitch" on fault detectors.

6.13	On Rectifier HCS Defeater panels, attempt a fault detector reset and confirm permissive blocking feature.

7.0	FINAL CONDITIONS

7.1 	Remove all temporary test fixtures:

•  Rectifier HCS Defeater panels in NORMAL

•  red keys

•  K4 pick-up device

7.2	 Obtain EIC sign-off.  _______________  Date:  ____________

ECS HCS I/O CHECKOUT RECORD

TEST PERSONNEL:___________________		DATE: _________________

NSTX CBD Name.....................................................	TF	OH	PF1	PF2

TFTR CBD Name......................................................	(TF1)	(TF2)	(EF)	(OH)

6.1 	Inspect HCS cabinet		___	___	___	___

6.2 	HCS Defeaters in TEST		___	___	___	___

6.3 	Clear rectifier L3 faults, clear non-rectifier L1 faults		___	___	___	___

6.4 	Defeat K4 HIS enable		___	___	___	___

6.5 	Reset HCS L1 and L3 using K6, confirm HCS L1 & L3 lamps	___	___	___	___

6.6 	Confirm HCS Defeater L1 & L3 green Led's		___	___	___	___

6.7 	Confirm no faults w/control power off on HCS Defeater unit	___	___	___	___

6.8 	HCS Defeaters in NORMAL		___	___	___	___

6.9 	Turn off control power of each unit, confirm L3 and red LED	___	___	___	___

on HCS Defeaters

6.10 	Initiate a L1 fanult and confirm L1 and red LED on HCS Defeaters	___	___	___	___

6.11	Confirm no fault detector permissive LED's lit		___	___	___	___

6.12 	Insert red key in 69TPS, confirm FD Ready glitch and  permissive

LED on each unit, and HCS permissive lamp on control board	___	___	___	___

6.13 	Confirm permit/reset interlock on HCS Defeater units	___	___	___	___

6.7 HCS Def	6.9 L3 HCS flt	6.10 L1 HCS flt	6.11 FD Perm LED  	6.12 FD Ready

No HCS Fault w/	   w/cont power	    w/red devil out	    off w/permit off        	Glitch

cont power off	   off

TF1-1	__	__	__	   __	__

TF1-2 	__	__	__	   __	__

TF1-3 	__	__	__	   __	__

TF1-4 	__	__	__	   __	__

TF1-5 	__	__	__	   __	__

TF1-6 	__	__	__	   __	__

TF1-7 	__	__	__	   __	__

TF1-8 	__	__	__	   __	__

TF1-9 	__	__	__	   __	__

TF1-A 	__	__	__	   __	__

TF2-1 	__	__	__	   __	__

TF2-2 	__	__	__	   __	__

TF2-3 	__	__	__	   __	__

TF2-4 	__	__	__	   __	__

TF2-5 	__	__	__	   __	__

TF2-6 	__	__	__	   __	__

TF2-7 	__	__	__	   __	__

TF2-8 	__	__	__	   __	__

TF2-9	__	__	__	   __	__

TF2-A 	__	__	__	   __	__

OH1-1	__	__	__	   __	__

OH1-2 	__	__	__	   __	__

OH2-1 	__	__	__	   __	__

OH3-1 	__	__	__	   __	__

OH3-2 	__	__	__	   __	__

OH4-1	__	__	__	   __	__

OH5-1 	__	__	__	   __	__

OH5-2 	__	__	__	   __	__

OH6-1	__	__	__	   __	__

EF1-1 	__	__	__	   __	__

EF1-2 	__	__	__	   __	__

EF2-1 	__	__	__	   __	__

EF2-2 	__	__	__	   __	__

EF3-1 	__	__	__	   __	__

EF3-2 	__	__	__	   __	__

EF4-1 	__	__	__	   __	__

EF4-2 	__	__	__	   __	__

HF 	__	__	__	   __	__