Procedure Title: ECS THYRISTOR RECTIFIER REACTIVATION FOLLOWING EXTENDED SHUTDOWN

| Number: OP-PC-734 | Revision: 0 | Effective Date: 11/9/98 (Ref. OP-AD-97 Expiration Date: (2 yrs. unless otherwise stipulated) |
| --- | --- | --- |

Procedure Approvals

| Author C Neumeyer | Date |
| --- | --- |

| ATI S Ramakrishnan | Date |
| --- | --- |

| RLM C Neumeyer | Date |
| --- | --- |

Responsible Division: NSTX WBS-5

Procedure Requirements designated by RLM

|  | NSTX Work Permit (TBD) | ✓ | Lockout/Tagout (OP-AD-61) |
| --- | --- | --- | --- |

|  | TFTR Work Permit (OP-AD-09) |  | Door Permit (OP-G-93) |
| --- | --- | --- | --- |

|  | Tritium Work Permit (OP-AD-49) | ✓ | T-Mod (OP-AD-03) |
| --- | --- | --- | --- |

|  | RWP (HP-OP-20) |  | Lift Procedure (ENG-021) |
| --- | --- | --- | --- |

|  | Confined Space Permit |  | DCA/DCN (OP-AD-104) |
| --- | --- | --- | --- |

|  | Pre-Job Brief (OP-AD-79) |  | ATI Walkdown |
| --- | --- | --- | --- |

|  | USQD (OP-AD-63) |  | Independant Review |
| --- | --- | --- | --- |

|  | Master Equip. List Mod (OP-AD-112) |  | ES&H Review (NEPA, IH, etc.) |
| --- | --- | --- | --- |

RUN COPY ASSIGNED TO RECTIFIER: E____-PSS-____ (TFTR Name) _____-PSS-_____S-_____P (NSTX Name) Engineering In Charge (EIC): ______________________ Date: ______/_______/_______ Special Instructions:

REVIEWERS (designated by RLM)

ATI - S Ramakrishnan

Test Director – J Corl

Independent Reviewer

D-Site Shift Supervisor

NSTX – C Neumeyer

TFTR Caretaking

Vacuum

Computer

Tritium

QA/QC

AC Power – A Ilic

FED

ECS/MG – D McBride , E Baker

ERWM

Water

NB

RF

Diagnostics

TRAINING (designated by RLM)

| No training required ______________ | Instructor _____________________________ |
| --- | --- |

| Personnel (group, job title or individual name) | Read Only | Instruction | Hands On |
| --- | --- | --- | --- |

| FCPC Technicians and Engineers | ✓ |  |  |
| --- | --- | --- | --- |

Training Rep. ____________________________________

RLM____________________________________

1.0	Purpose

This  procedure covers activities related to the reactivation of ECS Thyristor Rectifiers following extended shutdown.

2.0	Scope

2.1 Listed below are the ECS Rectifiers that are covered by this procedure, by TFTR name and by NSTX name.  There will be a separate copy of this procedure for each rectifier to be maintained.

| TFTR | NSTX A section | NSTX B section |
| --- | --- | --- |

| ETF1-PS-1 | TF-PSS-1S-1P | TF-PSS-1S-2P |
| --- | --- | --- |

| ETF1-PS-2 | TF-PSS-1S-3P | TF-PSS-1S-4P |
| --- | --- | --- |

| ETF1-PS-3 |  |  |
| --- | --- | --- |

| ETF1-PS-4 |  |  |
| --- | --- | --- |

| ETF1-PS-5 |  |  |
| --- | --- | --- |

| ETF1-PS-6 |  |  |
| --- | --- | --- |

| ETF1-PS-7 |  |  |
| --- | --- | --- |

| ETF1-PS-8 |  |  |
| --- | --- | --- |

| ETF1-PS-9 |  |  |
| --- | --- | --- |

| ETF1-PS-A |  |  |
| --- | --- | --- |

| ETF2-PS-1 | OH-PSS-6S-1P |  |
| --- | --- | --- |

| ETF2-PS-2 | OH-PSS-6S-2P |  |
| --- | --- | --- |

| ETF2-PS-3 | OH-PSS-5S-1P |  |
| --- | --- | --- |

| ETF2-PS-4 | OH-PSS-5S-2P |  |
| --- | --- | --- |

| ETF2-PS-5 |  | OH-PSS-4S-1P |
| --- | --- | --- |

| ETF2-PS-6 |  | OH-PSS-4S-2P |
| --- | --- | --- |

| ETF2-PS-7 |  | OH-PSS-3S-1P |
| --- | --- | --- |

| ETF2-PS-8 |  | OH-PSS-3S-2P |
| --- | --- | --- |

| ETF2-PS-9 |  | OH-PSS-2S-1P |
| --- | --- | --- |

| ETF2-PS-A |  | OH-PSS-2S-2P |
| --- | --- | --- |

| EEF1-PS-1 | PF3U-PSS-2S-2P | PF3U-PSS-1S-2P |
| --- | --- | --- |

| EEF1-PS-2 | PF3L-PSS-2S-2P | PF3L-PSS-1S-2P |
| --- | --- | --- |

(con’t on next page)

| TFTR | NSTX A section | NSTX B section |
| --- | --- | --- |

| EEF2-PS-1 |  | OH-PSS-1S-1P |
| --- | --- | --- |

| EEF2-PS-2 |  | OH-PSS-1S-2P |
| --- | --- | --- |

| EEF3-PS-1 | PF1AL-PSS-2S | PF1AL-PSS-1S |
| --- | --- | --- |

| EEF3-PS-2 |  |  |
| --- | --- | --- |

| EEF4-PS-1 | PF1B-PSS-2S | PF1B-PSS-1S |
| --- | --- | --- |

| EEF4-PS-2 | PF1AU-PSS-2S | PF1AU-PSS-1S |
| --- | --- | --- |

| EFVC-PS-1 |  |  |
| --- | --- | --- |

| EHF-PS |  |  |
| --- | --- | --- |

| EOH1-PS-1 | CHI-PSS-1S-1P | CHI-PSS-2S-1P |
| --- | --- | --- |

| EOH1-PS-2 | CHI-PSS-1S-2P | CHI-PSS-2S-2P |
| --- | --- | --- |

| EOH2-PS-1 | PF3U-PSS-2S-1P | PF3U-PSS-1S-1P |
| --- | --- | --- |

| EOH3-PS-1 | PF2L-PSS-2S | PF2L-PSS-1S |
| --- | --- | --- |

| EOH3-PS-2 |  |  |
| --- | --- | --- |

| EOH4-PS-1 | PF3L-PSS-2S-1P | PF3L-PSS-1S-1P |
| --- | --- | --- |

| EOH5-PS-1 | PF2U-PSS-2S | PF2U-PSS-1S |
| --- | --- | --- |

| EOH5-PS-2 |  | PF4/5-PSS-2S |
| --- | --- | --- |

| EOH6-PS-1 | PF4/5-PSS-3S | PF4/5-PSS-1S |
| --- | --- | --- |

2.2 Following activities are included in this procedure. The EIC shall select, for each rectifier under test, which of the activities are to be included.

| Para. | Check | Include |
| --- | --- | --- |

| 5.1 | Visual inspection |  |
| --- | --- | --- |

| 5.2 | T-mod disposition |  |
| --- | --- | --- |

| 5.3 | Disconnect/Bypass resistance measurement |  |
| --- | --- | --- |

| 5.4 | Cooling water leakage/flow switch check |  |
| --- | --- | --- |

| 5.5 | Hipot Line-Line |  |
| --- | --- | --- |

| 5.6 | Hipot Line-Ground |  |
| --- | --- | --- |

| 5.7 | Control power supply check |  |
| --- | --- | --- |

| 5.8 | MGD functionality test |  |
| --- | --- | --- |

| 5.9 | FG functionaility test |  |
| --- | --- | --- |

| 5.10 | Opto-Isolator Tests |  |
| --- | --- | --- |

| 5.11 | Central I&C interface test |  |
| --- | --- | --- |

| 5.12 | AC Power confirmation & Feeder Breaker interlock |  |
| --- | --- | --- |

| 5.13 | FD/FG Settings |  |
| --- | --- | --- |

EIC Responsible for execution of this procedure:

Init.

3.0	References, Drawings, and Procedures

3.1	Environment, Safety, and Health Manual 5008, Section 2 and 9.

3.2	Complete books of Transrex EMDRAC and CWD drawings.

3.3	AP-ECS-001, Rev. 8 FCPC Systems Access Procedure

3.4	Operator Aid 93-1028-30 - Instructions for ECS Stand-Alone Tester

3.5	Operator Aid OA-40 – Operation Instructions for the 2.5kV Hipotter (Thumper)

3.6	OP-PC-735 – ECS Thyristor Settings Procedure

4.0	Prerequisites

CONFIRM access procedure AP-ECS-001, Rev. 8  in effect.

Init.________

NOTE: If conditions for access are different than those called out by the above procedure, note same and attach to run copy of this procedure.

EIC

5.0	 Procedures

5.1	 Visual Inspection

Access the rectifier and inspect for abnormalities, correct as required, report any evidence of degradation to EIC.

Init.________

5.2	T-mod Disposition

Investigate any T-mods in place and make appropriate repairs/corrections as required to permit remove same, in accordance with T-Mod Procedure OP-AD-03.

Init.________

5.3	Disconnect/Bypass Resistance Measurement

Remove disconnect switch compartment cover panels as required to gain access to the Pringle switch. Measure and record resistances using Digital Low Resistance Ohmmeter.

| Switch Position | Between Terminals | A Section (µΩ) | B Section (µΩ) |
| --- | --- | --- | --- |

| Line | (+) Rectifier to (+) Load |  |  |
| --- | --- | --- | --- |

| Line | (-) Rectifier to (-) Load |  |  |
| --- | --- | --- | --- |

| Bypass | (+) Load to Bypass Link |  |  |
| --- | --- | --- | --- |

| Bypass | (-) Load to Bypass Link |  |  |
| --- | --- | --- | --- |

Init.________

5.4	Cooling Water Leak Check

5.4.1	Request D-site water systems operator to energize FCPC cooling water system. Open water supply valve to rectifer. Check, after an interval of at least 30 minutes, for evidence of water leaks. Make repairs as necessary.

Init.________

5.4.2	Shut water supply valve and confirm dropout of water flow switch.

Init.________

5.5	Hipot Line-Line

5.5.1	Open and tag out converter transformer 13.8kV primary disconnect switch to rectifier under test, in accordance with Lockout/Tagout Procedure OP-AD-61.

Init.________

5.5.2	Place Disconnect/Bypass switch in bypass position, both A and B sections. Remove disconnect switch compartment cover panels as required to gain access to the Pringle switch. Apply safety grounds to the load side of both the A and B sections.

Init.________

5.5.3	Confirm that Card Reader Access to FCPC is in effect. Announce over the D-site PA system that hipot testing is underway in the FCPC building and that the 1st  floor FCPC areas, as well as the FCPC transformer yards, are off limits to unauthorized personnel until further notification. Energize FCPC 1st floor flashing red lights.

Init.________

5.5.4	Execute Operator Aid Procedure OA-40, “Operation Instructions for the 2.5kV Hi-Potter (Thumper)”, section on Rectifier Section Testing (individual rectifier and bypass module testing not required), one section at a time, for each section, other section jumpered and grounded.

NOTES:

1)	During these tests, jumpered 3-phase AC buses shall remain grounded at all times.

Init.________

5.5.5	When hipot testing session is completed, announce same over D-site PA system and turn off FCPC flashing lights.

Init.________

5.5.6	Confirm that all jumpers and grounds have been removed.

Init.________

5.6	Hipot Line-Ground

5.6.1	Open and tag out converter transformer 13.8kV primary disconnect switch to rectifier under test, in accordance with Lockout/Tagout Procedure OP-AD-61.

Init.________

5.6.2	AC Power group to apply three phase ground on AC side of converter transformer under test, either locally at the converter transformer primary or via the ground & test breaker on SV1 and/or SV2.

AC Power Engineer:

Date & Time:								Init.________

5.6.3	Place Disconnect/Bypass switch in bypass position, both A and B sections. Remove disconnect switch compartment cover panels as required to gain access to the Pringle switch. Apply safety grounds to the load side of both the A and B sections.

Init.________

5.6.4	Access rear of rectifier cabinet and jumper together AC and DC bus bars of both sections. Ground section not under test.

Init.________

5.6.5	Confirm that Card Reader Access to FCPC is in effect. Announce over the D-site PA system that hipot testing is underway in the FCPC building and that the 1st floor FCPC areas, as well as the FCPC transformer yards, are off limits to unauthorized personnel until further notification. Energize FCPC 1st floor flashing red lights.

Init.________

5.6.6	Apply a 1 minute 15kV DC hipot, one section at a time, to ground, with the other section grounded. Record leakage current.

NOTES:

1)	During these tests, jumpered 3-phase AC buses shall remain grounded at all times.

2) During these tests, water flow shall be maintained in the rectifer under test.

Leakage Current: 	A Section: _______		B Section:

Init.________

5.6.7	Confirm that all jumpers and grounds have been removed.

Init.________

5.7 Control Power Supply Check

Confirm output voltages and ripple of control/logic power supplies.  If necessary, adjust power supplies to the manufacturer’s specified output voltage. Check for excessive rms ripple on the power supply output.  Ripple should not exceed 3% of the full rated output voltage.

| Pwr Sup No. | Voltage & Tolerance | Terminals | Voltage | Ripple |
| --- | --- | --- | --- | --- |

| PS1 | +24VDC, +1.2V (+22.8 to +25.2V) | +A2TB5-12 -A2TB5-13 |  | ____mV, <720mV |
| --- | --- | --- | --- | --- |

| PS2 | +5VDC, +0.25V (+4.75 to +5.25V) | +A2TB5-17 -A2TB5-13 |  | ____mV, <150mV |
| --- | --- | --- | --- | --- |

| PS3 | +15VDC, +0.75V (+14.25 to +15.75V) | +A2TB5-14 -A2TB5-13 |  | ____mV, <450mV |
| --- | --- | --- | --- | --- |

| PS4 | -15VDC, +0.75V (-15.75 to –14.25V) | -A2TB5-16 +A2TB5-13 |  | ____mV, <450mV |
| --- | --- | --- | --- | --- |

| PS5 | +5VDC, +0.25V (+4.75 to +5.25V) | +A2TB5-19 -A2TB5-13 |  | ____mV, <150mV |
| --- | --- | --- | --- | --- |

Init.________

5.8		Master Gate Driver Functionality Test

5.8.1	Place HCS Defeater in the TEST position.

Init.________

5.8.2	Turn on the Convert, Block Bypass, FD Ready, and MGD Enable toggle switches.

Init.________

Note:  Central I&C may over-ride the convert bit.  If so, using the stand-alone tester, give a hexadecimal OFF command to clear.

5.8.3	CONFIRM that all power module MGDs are firing; which is indicated by the illumination of the red and green LEDs.

Init.________

5.8.4	Turn the FD Ready and MGD Enable toggle switches off.  CONFIRM the following:

a)  All power module MGDs OFF.	Init.________

b)  All bypass module MGDs ON.	Init.________

5.8.5	Turn the FD Ready and MGD Enable toggle switches on.  CONFIRM the following:

a)  All power module MGDs ON.	Init.________

b)  All bypass module MGDs OFF.	Init.________

5.8.6	With the FD Ready, Convert, and MGD Enable toggle switches on, turn the Block Bypass toggle switch off.  CONFIRM the following:

a)  All power module MGDs are firing.	Init.________

b)  All bypass module MGDs are firing.	Init.________

Init.________

5.9	FG Functionality Test

5.9.1	Disconnect PT inputs and connect temporary synchronizing voltage source to A2/TB1-3,4,5,6. Confirm FG phase lock action and FG Ready signals.

Init.________

5.9.2	Using the Stand-Alone Tester confirm proper waveform and amplitude for the rectifier alpha signals per the following steps (Refer to Operator Aid 93-1028-30 - Stand-Alone Tester Program).

NOTE:   alpha voltage/degrees (SCR firing angle) is as follows…

• 0.0557V/degree.  (9.2 volts = 165o) at FG slot A14-M

5.9.2.1	Set up Stand Alone to issue α = 165o. Confirm A14 pin M voltages per the above specifications.

Init.________

5.9.2.2	Use Stand Alone to issue α test waveform. Confirm A14 pin M firing generator waveform is symmetrical and free of notches or jagged waveform indicating bad or missing bits.

Init.________

5.10	Opto-Isolator Boards

5.10.1	Test and repair all spare channels on the A5 and A8 opto-isolator boards.  If any of these spare channels are in use, repair and restore the original channel.

5.10.2 Confirm the proper output voltage levels on the Level 1 and 3 opto-isolators using the following method.

• Confirm that the Hardwired Defeater bat handle is set to the TEST position.

• For Level 1 test, connect a DC voltmeter either on TP5 of the Go Card or to A1A8TB2-2, referenced to signal ground.

• Lift wire 88 connected to A1A8TB3-1.

• Connect a 1.5 volt battery across:  + A1A8TB3-1 and - A1A8TB3-2.

• The voltage on the voltmeter should be +15 volts +0, -2 volts.  If not, replace the opto-isolator.

• Re-connect wire 88 on A1A8TB3-1.

Init.________

• For Level 3 test, connect a DC voltmeter either on TP4 of the Go Card or to A1A8TB2-4, referenced to signal ground.

• Lift wire 90 connected to A1A8TB3-3.

• Connect a 1.5 volt battery across:  + A1A8TB3-3 and - A1A8TB3-4.

• The voltage on the voltmeter should be +15 volts +0, -2 volts.  If not, replace the opto-isolator.

• Re-connect wire 90 on A1A8TB3-3.

Init.________

5.11	Central I&C Interface Test

Confirm the Central I&C mimic page display of the following:

• Rear doors open/closed

• Section A Disconnect/Bypass switch line/bypass positions

• Section B Disconnect/Bypass switch line/bypass positions

NOTE: If Central I&C not available, check for transition of LED bit indicators on appropriate 322 Digital Input Module.

Init.________

5.12	AC Power Confirmation & Feeder Breaker Test

5.12.1	AC Power Group confirmation of AC protective relay settings.

NOTE: Attach relay test data sheets to this procedure for 50D-1, 50D-2, 50/51, 50G, and 49 relays.

AC Power Engineer: 							Init.________

5.12.2	AC Power Group permission to operate 13.8kV SV feeder breaker (no load)

AC Power Engineer: 							Init.________

5.12.3 Perform the following tests of the feeder breaker interlocking:

• Place HCS Defeater in TEST position. Close feeder breaker, observe transiton of CB Advance Trip LED on Fault Detector

Init.________

• Turn OFF rectifier control power, and confirm that feeder breaker does not trip (HCS Defeater in TEST position).

Init.________

• Push HCS Defeater CB Trip button, confirm that feeder breaker trips.

Init.________

• Place HCS Defeater in NORMAL position. Close feeder breaker. Turn OFF rectifier control power, and confirm that feeder breaker trips.

Init.________

• Close feeder breaker. Push local FCPC e-stop and confirm breaker trip.

Init.________

5.12.4	AC Power Group permission to energize 13.8kV feeder and converter transformer.

AC Power Engineer:

Date & Time:								Init.________

5.13	FD/FG Settings

Adjust all settings in accordance with OP-PC-735 – ECS Thyristor Settings Procedure. Note: It is essential that a fresh run copy of this procedure be used since administrative current limits for coils are subject to change.