| Procedure Title: ECS THYRISTOR RECTIFIER FAULT DETECTOR SETTINGS PROCEDURE FOR NSTX |
| --- |
| Number OP-PC-735 | Revision: 3 | Effective Date: 03/07/05 Expiration Date: _____ (2 yr. unless otherwise stipulated) |
| Procedure Approvals |
| Author C. Neumeyer | Date _____ |
| ATI S. Ramakrishnan | Date _____ |
| RLM A. Von Halle | Date _____ |
| Responsible Division: NSTX |
| Procedure Requirements Labwide: |
|  | Work Planning Form #__(ENG-032) |  | Lockout/Tagout (ESH-016) |
|  | Confined Space Permit (5008, Sec. 8, Chap 5) |  | Lift Procedure (ENG-021) |
|  | Master Equip. List Mod (GEN-005) |  | ES&H Review (NEPA, IH, etc.) |
|  | RWP (HP-OP-20) |  | Independent Review |
|  | ATI Walkdown |  | Pre-job Brief |
|  | Post-job Brief * |  |  |
| D-Site Specific: |
|  | D-Site Work Permit (OP-AD-09) |  | Door Permit (OP-G-93) |
|  | Tritium Work Permit (OP-AD-49) |  | USQD (OP-AD-63) |
|  | Pre-job brief (OP-AD-79) |  | T-MOD (OP-AD-03) |
|  | DCA/DCN (OP-AD-104) # _____ |  |  |

REVIEWERS (designated by RLM)

Accountable Technical Individual _____

Test Director _____

Independent Reviewer _____

D-Site Shift Supervisor _____

NSTX A. VonHalle

TFTR Caretaking _____

Vacuum _____

Computer _____

Tritium _____

Quality Assurance/Quality Control _____

AC Power A. Ilic

Maintenance and Operations Division _____

Energy Conversion System/MG System S. Ramakrishnan, E. Baker

Environmental Restoration & Waste Management Division _____

Water _____

Neutral Beam (Heating Systems Branch of Electrical Engineering) _____

Radiofrequency (Heating Systems Branch of Electrical Engineering) _____

Diagnostics _____

Environmental, Safety, & Health _____

| TRAINING (designated by RLM) No training required Instructor _____ |
| --- |
| Personnel (group, job title or individual name) | Read Only | Instruction | Hands-On |
| Training Rep. ____________________________________ |  |  |  |
| RLM ____________________________________ |  |  |  |

1.0	Purpose

This  procedure covers the setting of Fault Detector (FD) protective levels for the  ECS Thyristor Rectifiers. It also serves to communicate information to AC Power personnel for their use in establishing 13.8kV feeder breaker AC protective relay settings. It is intended for use when changes are to be made to the administrative limits imposed on the NSTX coil currents via ISTP-NSTX-001. It is not intended for temporary changes to be made in the field to overcome control/instrumentation difficulties sometimes encountered with ECS Thyristor Rectifier operations; such circumstances shall be addressed on a case by case basis via the T-mod procedure OP-AD-03.

2.0	Scope

2.1 Listed below are the ECS Rectifiers that are covered by this procedure, by TFTR name and by NSTX name.

| NSTX | TFTR Name |
| --- | --- |
| Ckt.# | Coil | NSTX Name |  |
| P1 | TF | TF-PSS-1S-1P | ETF1-PSS-1A |
|  |  | TF-PSS-1S-2P | ETF1-PSS-1B |
|  | TF Spare | TF-PSS-2S-1P | ETF1-PSS-3A |
|  |  | TF-PSS-2S-2P | ETF1-PSS-3B |
| P1 | TF | TF-PSS-1S-3P | ETF1-PSS-2A |
|  |  | TF-PSS-1S-4P | ETF1-PSS-2B |
| P1 | TF Spare | TF-PSS-2S-3P | ETF1-PSS-4A |
|  |  | TF-PSS-2S-4P | ETF1-PSS-4B |
|  |  | TF-PSS-3S-1P | ETF1-PSS-5B |
|  |  | TF-PSS-3S-2P | ETF1-PSS-5A |
|  |  | TF-PSS-4S-1P | ETF1-PSS-7B |
|  |  | TF-PSS-4S-2P | ETF1-PSS-7A |
|  |  | TF-PSS-5S-1P | ETF1-PSS-9B |
|  |  | TF-PSS-5S-2P | ETF1-PSS-9A |
|  |  | TF-PSS-3S-3P | ETF1-PSS-6B |
|  |  | TF-PSS-3S-4P | ETF1-PSS-6A |
|  |  | TF-PSS-4S-3P | ETF1-PSS-8B |
|  |  | TF-PSS-4S-4P | ETF1-PSS-8A |
|  |  | TF-PSS-5S-3P | ETF1-PSS-AB |
|  |  | TF-PSS-5S-4P | ETF1-PSS-AA |

| P2 | OH | OH-PSS-1S-1P | ETF2-PSS-7B |
| --- | --- | --- | --- |
|  |  | OH-PSS-2S-1P | ETF2-PSS-7A |
|  |  | OH-PSS-3S-1P | ETF2-PSS-5B |
|  |  | OH-PSS-4S-1P | ETF2-PSS-5A |
|  |  | OH-PSS-8S-2P | ETF2-PSS-2A |
|  |  | OH-PSS-7S-2P | ETF2-PSS-2B |
|  |  | OH-PSS-6S-2P | ETF2-PSS-4A |
|  |  | OH-PSS-5S-2P | ETF2-PSS-4B |
|  |  | OH-PSS-5S-1P | ETF2-PSS-3B |
|  |  | OH-PSS-6S-1P | ETF2-PSS-3A |
|  |  | OH-PSS-7S-1P | ETF2-PSS-1B |
|  |  | OH-PSS-8S-1P | ETF2-PSS-1A |
|  |  | OH-PSS-4S-2P | ETF2-PSS-6A |
|  |  | OH-PSS-3S-2P | ETF2-PSS-6B |
|  |  | OH-PSS-2S-2P | ETF2-PSS-8A |
|  |  | OH-PSS-1S-2P | ETF2-PSS-8B |
|  |  | SPARE | ETF2-PSS-9A |
|  |  | SPARE | ETF2-PSS-9B |
|  |  | SPARE | ETF2-PSS-AA |
|  |  | SPARE | ETF2-PSS-AB |
| P3 | PF1aU | PF1AU-PSS-1S-1P | EEF4-PSS-2B |
|  |  | PF1AU-PSS-1S-2P | EOH3-PSS-2B |
|  |  | PF1AU-PSS-2S-1P | EEF4-PSS-2A |
|  |  | PF1AU-PSS-2S-2P | EOH3-PSS-2A |
| P4 | PF1aL | PF1AL-PSS-1S-1P | EEF3-PSS-1B |
|  |  | PF1AL-PSS-1S-2P | EEF3-PSS-2B |
|  |  | PF1AL-PSS-2S-1P | EEF3-PSS-1A |
|  |  | PF1AL-PSS-2S-2P | EEF3-PSS-2A |
| P5 | PF1b | PF1B-PSS-1S | EEF4-PSS-1B |
|  |  | PF1B-PSS-2S | EEF4-PSS-1A |
| P6 | PF2U | PF2U-PSS-1S | EOH5-PSS-1B |
|  |  | PF2U-PSS-2S | EOH5-PSS-1A |
| P7 | PF2L | PF2L-PSS-1S | EOH3-PSS-1B |
|  |  | PF2L-PSS-2S | EOH3-PSS-1A |
| P8 | PF3U | PF3U-PSS-1S-1P | EOH2-PSS-1B |
|  |  | PF3U-PSS-1S-2P | EEF1-PSS-1B |
|  |  | PF3U-PSS-2S-1P | EOH2-PSS-1A |
|  |  | PF3U-PSS-2S-2P | EEF1-PSS-1A |
| P9 | PF3L | PF3L-PSS-1S-1P | EOH4-PSS-1B |
|  |  | PF3L-PSS-1S-2P | EEF1-PSS-2B |
|  |  | PF3L-PSS-2S-1P | EOH4-PSS-1A |
|  |  | PF3L-PSS-2S-2P | EEF1-PSS-2A |
| P10 | PF5 | PF5-PSS-1S | EOH6-PSS-1B |
|  |  | PF5-PSS-2S | EOH5-PSS-2B |
|  |  | PF5-PSS-3S | EOH6-PSS-1A |
| P11 | CHI | CHI-PSS-1S-1P | EOH1-PSS-1B |
|  |  | CHI-PSS-1S-2P | EOH1-PSS-2B |
|  |  | CHI-PSS-2S-1P | EOH1-PSS-2A |
|  |  | CHI-PSS-2S-2P | EOH1-PSS-1A |
| P12 | PF4 | PF4-PSS-1S | EEF2-PSS-1B |
|  |  | PF4-PSS-2S | EEF2-PSS-1A |
| P13 | SPA/RWM | P13-PSS-1S | EEF2-PSS-2B |
|  |  | P13-PSS-2S | EEF2-PSS-2A |

3.0	References, Drawings, and Procedures

3.1 ISTP-NSTX-001, “NSTX Coil Energization Tests”

3.2 Complete book of Transrex EMDRAC drawings.

4.0	Prerequisites

Execution of this procedure impacts the levels of overcurrent and overtime protection provided by the ECS Thyristor Rectifiers for the NSTX machine. Therefore it shall only be executed in conjunction with ISTP-NSTX-001 which is used to administratively control NSTX operating limits, according to instructions issued by the Test Director for same.

5.0	 Procedures

5.1	Confirm control power on, 13.8kV feeder breakers open.

5.2	Confirm up to date calibration of Digital Volt Meter (DVM) to be used to execute this procedure.

5.3	Adjust all settings called out in column labeled “Set” on attached spreadsheet entitled “OP-PC-735 Settings”.